SPECIFICATION TEMPLATE

FUNDERMAX Max Exterior F-Quality High Pressure Laminate Panel

- SCOPE OF WORK

The scope of work includes the design, supply, fabrication and installation of FUNDERMAX cladding material, complete with all necessary sub-structures, anchors, hardware and fittings to provide a total installation from the structure out.

- MATERIAL AND FINISHES

Cladding Material:

FUNDERMAX Max Exterior F-Quality High Pressure Laminate cladding material supplied by Blue Chip Group Pty Ltd (Ph: 08 9451 2344) shall be duromer high-pressure laminates (HPL) produced in accordance with EN 438-6 Type EDF with double-hardened acrylic PUR resins. Produced in lamination presses under great pressure and high temperature the double-hardened acrylic PUR resins provide extremely effective weather protection that is particularly suitable for long-lasting balconies and façade claddings. The material shall be flame-retardant according to Fire Test EN 13501-1, B-s2, d0.

Colour Selection:

Refer to exterior finishes schedule.

(Select colour code/s from the Finishes tab at the below link) http://www.bluechipgroup.net.au/natural-cladding-perth/fundermax-perth.html

Material Properties:

As a standard, the Max Exterior panels come printed on both sides. The core contains phosphate based flame-retardant which achieves 0 for spread-of-flame when tested to AS 1530.3 and the surface is lightfast thanks to the double-hardened resin making it extremely weather resistant.

Mechanical Properties

| Apparent density | EN ISO 1183-1 | g/cm3 | ≥ 1.35 |
| --- | --- | --- | --- |
| Flexural strength | EN ISO 178 | MPa | ≥ 80 |
| Modulus of elasticity | EN ISO 178 | MPa | ≥ 9.000 |
| Coefficient of thermal expansion | DIN 52328 | 1/K | 18 x 10-6 |
| Thermal conductivity |  | W/mK | 0.3 |
| Water vapour diffusion resistance |  |  | ca. 17.200 μ |
| Artificial weathering | EN ISO 4892-2 3000 h | EN 20105-A02 greyscale | 4-5 |

Fire Properties

| Australia | AS 1530.3 - Ignitability - Spread of flame - Heat evolved - Smoke developed | 13 0 0 4 |
| --- | --- | --- |
|  | AS 3837 Average specific extinction area | Group 3 15.4 m2/Kg |
| Europe | EN13501-1 | B-s2, d0 |
| Germany | DIN 4102 | B1 for 6 - 10mm |
| France | NFP 92501 | M1 for 2 - 10mm |
| Spain | UNE 23727-90 | M1 for 6 - 10mm |
| USA | ASTM E84-15 - Classification - Flame Spread (FSI) - Smoke Developed (SDI) | A 15 70 |

Panel Weight

| 6mm | 8mm | 10mm | 12mm |
| --- | --- | --- | --- |
| 8.7 kg/m2 | 11.6 kg/m2 | 14.5 kg/m2 | 17.4 kg/m2 |

Tolerances in accordance with EN 438-6, 5.3

| Thickness 6mm Panel | ±0.4mm |
| --- | --- |
| Thickness 8mm Panel | ±0.5mm |
| Length | ± 10mm |
| Width | ± 10mm |

Fixings:

Fasteners, including concealed screws, nuts, bolts and other items required for connecting aluminium to aluminium or aluminium to steel shall be in accordance with AS 3566.2 and of a type to suit its application and exposure conditions.

Class 1/2:	Internal applications.

Class 3:	External applications, moderate industrial and marine applications.

Class 4:	Severe marine applications

All fixing anchors, brackets and similar attachments used in the erections, shall be of aluminium, non-magnetic stainless steel, zinc coated steel, or hot dip zinc galvanised steel.

Dissimilar Materials:

Where two surfaces of dissimilar material come into contact, such surfaces shall be separated with a layer of PVC or Polyethylene tape or powder-coat finish.

Warranty:

FUNDERMAX shall be covered by a manufacturer’s warranty for a minimum period of 10 years. All work to be carried out in accordance with the FUNDERMAX technical recommendations and installation details. Life Expectancy: 33+ years

- INSTALLATION

The cladding system shall be installed by an approved cladding subcontractor with a demonstrated experience of at least 5 years in the fabrication and installation of pre-finished cladding systems. All work to be carried out in accordance with the FUNDERMAX manufacturer's recommendations and installation manuals. The cladding shall be fixed onto the STUDTEK Façade system supporting sub-structure behind and a construction joint of 8-10mm (nominal) shall be provided between cladding panels. All fixing and joint details shall be designed to provide for the expected thermal and structural movements. In order to form a water-resistant seal, apply a suitable weather seal gasket to all vertical panel joints and a horizontal backing strip to all horizontal joints. Use a suitable sealant for the corners, horizontal joints and other areas as required. Allow for perforated flashings to be applied to the top and bottom of the façade wall to allow required ventilation. All component parts shall be installed level, true to line with uniform joints and reveals.

Sarking:

Shall be FIRESPAN deemed-to-satisfy non-combustible sarking tested by a NATA accredited laboratory to AS 1530.1. Install and tape in accordance with AS 4200.2 to all cladding areas.

Sub-framing System:

The sub-framing system to be attached to the main structure in a manner to ensure all applied loadings to the cladding is transferred back to the main structure. Size and spacing of top hat members shall be determined according to applied loads and deflection limitations. Top-hat spacings shall be maximum 600mm to adequately support the cladding system.

Acceptable Sub-framing manufacturers are:

- STUDTEK Facade Framing, 08 9451 2344, sales@bluechipgroup.net.au.

Standards

STUDTEK Zincalume Facade Framing is cold-formed according to AS/NZS:4600 from Zincalume G300 steel which is continuous hot-dipped aluminium/zinc alloy-coated structural steel as per AS:1397.

Panel Edge Treatment:

No edge treatment required.

Installation System Code:

FX-06-VRF: Visible Rivet Fix

FX-06-VSF: Visible Screw Fix (timber batten)

FX-06-CAF: Concealed Adhesive Fix

(PDF & DWG construction details available on request)

(Delete options not required)

Disclaimer:

This Specification provided is generic in nature and is supplied in good faith for Specification guidance purposes only. It is understood that no 2 projects are alike and project specific information and advice should be obtained from necessary engineers, consultants and suppliers on a project to project basis.